## Logos (hidden)
Official (as one object)
Grouped
One object
PACIFIC POWER ROCKY MOUNTAIN POWER
A DIVISION OF PACIFICORP A DIVISION OF PACIFICORP

## Cover Sheet
Web Sites:
https://www.rockymountainpower.net/working-with-us/business-customers/arc-flash-fault-current.html
https://www.pacificpower.net/working-with-us/business-customers/arc-flash-fault-current.html
Revisions | Date
Cover Sheet - Added revision table | 2020-02-06 | R8
Fault Current Infinit Bus - Table 2: 208Y/120 Three Phase Pad Mounted Transformer, added impedance data for 1000kVA transformers | 2020-02-06
Request Form and Site Data Sheets: Updated options in delivery voltage dropdown list | 2020-03-24 | R9
Fault Current Infinit Bus - Table 6: 480/240 Single-Phase, Pad-Mounted and Overhead Transformers , new table added impedance data for 480/240V service voltages | 2020-11-16 | R10
Arc Flash
Arc flash analysis determines the arc flash boundary, the incident energy at working distance, and the level of personal protective equipment required for personnel to work within the arc flash boundary.
The Occupational Safety and Health Association (OSHA) and National Fire Protection Association (NFPA) mandate arc flash analysis to determine the Hazard Risk Category (HRC) which establishes the level of Flame Resistant (FR) clothing required for personal protection.
NFPA 70 E, Article 130.5 states, "The arc flash hazard analysis shall be updated when a major modification or renovation takes place, and is to be reviewed periodically, not to exceed 5 years.
Secondary Fault Current
NFPA 70 (National Electric Code), Article 110.24 requires electrical service panels be labeled with available fault current. This helps ensure properly sized equipment is installed, reducing the probability of damage caused by electrical faults.
Electrical power system fault duties tend to increase as systems are modified. Rocky Mountain Power and Pacific Power's policy is to provide secondary fault current at the transformer assuming an infinite source. Tables found in tab "Fault Current Infinite Bus" provide these values. Transformer size must be confirmed.
Customers must submit* the following information on the "Request Form":
· Facility Point Numbers(s) see Fig#1 on "Request Form" tab
· Service Voltage (240/120, 208Y/120, 480Y/277)
· Phase (Single-Phase, Three-Phase)
* Call 1-888-221-7070 for "Request Form" submittal information
Arc Flash Request
Upon receipt of completed "Request Form" customer is provided:
· System Impedance on primary side of distribution transformers
· Average transformer impedances
· Transformer fusing information
Secondary Fault Current Request
Upon receipt of completed "Request Form" customer is provided:
· Transformer size
· Fault Current Infinite Bus table
Disclaimer
Rocky Mountain Power and Pacific Power recommend customers de-energize electrical conductors when contact or faults are possible. In providing the information contained herein, the recipient acknowledges and understands that Rocky Mountain Power and Pacific Power provides this information based on the information in its files and other information available to it at the time of the request. The data will change over time based on changes in load and other dynamic elements of Rocky Mountain Power and Pacific Power's electrical system. Rocky Mountain Power and Pacific Power has not independently verified the accuracy of this information for the purposes for which it may be used by the recipient. Furthermore, recipient understands and acknowledges that Rocky Mountain Power and Pacific Power has no responsibility, liability, obligation or duty for the recipient’s electrical system and on the customer side of the electrical meter.
Commercial and Industrial Arc Flash and Secondary Fault Current Information Requests
Each year Rocky Mountain Power and Pacific Power provide arc flash and secondary fault current information to electrical consultants and electricians. To ensure consistency Rocky Mountain Power and Pacific Power utilize an Arc Flash/Secondary Fault Current "Request Form".

## Request Form (Customer)
Arc Flash and Secondary Fault Current Data Request Form
(Field Engineer sends this Form to Customer. Customer fill's out Form and returns it to Field Engineer)
Please submit a separate request for each site by duplicating this tab. Steps: 1) Fill in "Requestor Information, 2) Right click "Request Form (Customer) tab, 3) Move or Copy, 4) Select "Request Form (Customer), 5) Check "Create a Copy", 6) OK. Complete "Facility Location" section for each site.
Requester Information
Date of Request
Company Name
Contact Name
Mailing Address | Street Number
City, State, Zip
| Phone Numbers | Main:
Cell:
Email address
Facility Location
Company Name
Facility Name
* Facility Point Number
If possible provide a photo of the facility point tag. Please paste the photo in the cell to the right.
| Meter Number |  |  |  | Data for Drop Down Menu
| * Delivery Voltage | Dropdown Menu |  |  | Voltage | Phase
| * Phase | Dropdown Menu |  |  | Dropdown Menu | Dropdown Menu
| * Required Information |  |  |  | Single Phase: 120V, 2-Wire | Single Phase
Figure #1: Facility Point Examples |  |  |  |  | Single Phase: 120/240, 3-Wire | Three Phase
Pad Mounted Transformer |  |  | Pole Mounted Transformers |  | Single Phase: 240/480, 3-Wire
Three Phase: 208Y/120V, 4-Wire
Three Phase: 480Y/277V, 4-Wire
Three Phase: ∆ 120/240V, 4-wire
Three Phase: ∆ 240/480V, 4-wire
Three Phase: ∆ 480V, 3-Wire
Primary Delivery/Customer Owned Transformer
Other
Facility Point # = 05218092-173500
Note on C7: Name of the Engineering Firm, Consultant, or Electrician requesting information.
Note on C15: If the Company and Facility are located at the same site the Company Name and Facility Name may be the same. Some Companies have facilities located at different locations. In this case the Company and Facility Name will be different.
Note on C16: A unique Facility Name provides a way to differentiate between multiple facilities.
Note on C17: A Facility Point Number is a unique Rocky Mountain Power and Pacific Power identifier which defines a field site location. The facility point number tag is yellow having the parent company name "PacifiCorp". A photo of tag is preferred but numbers can be place in cell to right. This is a required field and all numbers are required. Photo example Facility Point Number: 05218092 - 173500
Note on C18: A photo is preferred and often simplifies communication.
Note on C19: Meter Number is not required, but can be added to the request form if available.
Note on D19: Optional. Not used.
Note on C20: The drop down menu contains common voltages. If service voltage is not listed in drop down select "Other Voltage" and enter actual voltage in cell to right. However it would be very unusual to specify "Other Voltage".

## Site Data (Utility)
Site Data
For Arc Flash request Field Engineer completes this Form and sends to Customer.
For Secondary Fault current request Field Engineer provides the transformer size information only.
Service Center
Address
Field Engineer
Phone Number
Primary System Fault Amps & Impedances
|  |  | Facility Information | [5 empty] | Do we need number of phases here?
|  |  | District | [5 empty] | We have voltage which is on "Request Form (Customer)" page.
|  |  | Substation | [5 empty] | Or can we get rid of voltage?
Circuit
Facility Point #
|  |  | Primary System Voltage | Drop Down Menu |  |  |  |  | Do not need this list
|  |  | Transformer Connection | Drop Down Menu |  |  |  |  | I referenced drop down
|  |  | Transformer Size / Type |  | Drop Down Menu |  |  |  | to list on "Request Form (Customer)" | Do not need
|  |  | Delivery Voltage (1) | Dropdown Menu |  | Data for drop down Menu |  |  |  | this list
|  |  | Transformer %Z | See Fault Current Infinite Bus Tab |  | Voltages | Transformer Connection | Xfmr Type | Secondary Voltage
|  |  | Secondary Conductor (2) |  |  | 2.4∆ | 1ph | Pole Mount | 480Y/277 | Xfmr Size
|  |  | Secondary Length (2) |  |  | 4.16Y | 3ph GrdWye-GrdWye | Padmount | 208Y/120 | Single Phase
|  |  | (1) Voltage as confirmed by Customer |  |  | 4.16∆ | 3ph Open Wye-Delta | Drop Down Menu | 480 Delta | 5
|  |  | (2) Secondary conductor information is provided |  |  | 7.2Y | 3ph Delta-GrdWye |  | 408Y/277 | 10
|  |  | when available. |  |  | 7.2∆ | 3ph Delta-Delta |  | 2400 | 15
[6 empty] | 7.62∆ | Customer Owned Transformer |  | 240 Delta | 25
|  |  | If service is primary metered only the primary system |  |  | 12.47Y | Drop Down Menu |  | 120/240 Single Phase | 37.5
|  |  | impedance at meter point is provided. |  |  | 13.2Y |  |  | 277 | 50
| Transformer & Service Diagram |  |  |  |  | 12∆ |  |  |  | 100
[6 empty] | 20.8Y |  |  |  | 167
|  |  | Protection |  |  | 14.4∆ |  |  |  | 250
|  |  | Transformer Fusing | See Fusing Tabs |  | 25Y |  |  |  | 333
[6 empty] | 19.9∆ |  |  |  | 500
|  |  | Field Engineer Provides: Arc Flash Request: 1) System Impedance on primary side of distribution transformers 2) "Fault Current Infinite Bus" tables showing average transformer impedances 3) Transformer fusing information Secondary Fault Current Request: 1) Transformer size 2) "Fault Current Infinite Bus" tables |  |  | 34.5Y |  |  |  | Three Phase
[6 empty] | Drop Down Menu |  |  |  | 75
112.5
150
225
500
750
1000
1500
2000
2500
3750
5000
Three Phase Banks
Note on F6: Field Engineer office
Note on F8: Field Engineer name
Note on H17: Transformer primary voltage

## Fault Current Infinite Bus
Short Circuit Transformer Bus Current Assuming an Infinite Bus1
Table 1: 480Y/277 Three Phase Pad Mounted Transformer
Information provided by Manufacturer
| Transformer kVA | Stock Number | % IR | %IX | X/R ratio | Transformer %Z | Calculated Fault Current (Amps) | NEMA Short Circuit Ratings
| 75 | 4710090 | 1.01 | 2.92 | 2.8911 | 1.62 | 5575.1802 | Panel | Rating
| 112.5 | 4700091 | 0.98 | 2.52 | 2.5714 | 2.7 | 5017.6622 | 100 | 10000
| 150 | 4700228 | 0.89 | 2.97 | 3.3371 | 3.18 | 5680.3723 | 400 | 22000
| 225 | 4700229 | 0.8 | 3.74 | 4.675 | 3.52 | 7697.5499 | 800 | 22000
| 300 | 4700094 | 0.78 | 3.66 | 4.6923 | 1.61 | 22439.2346 | 1600 | 65000
| 500 | 7991410 | 0.74 | 3.88 | 5.2432 | 1.94 | 31037.0856 | 3000 | 85000
| 750 | 7991371 | 0.73 | 5.68 | 7.7808 | 5.63 | 16042.2592 | 4000 | 85000
| 1000 | 9174749 | 0.62 | 5.74 | 9.2581 | 5.45 | 22096.127
| 1500 | 7992507 | 0.69 | 5.65 | 8.1884 | 5.46 | 33083.4868
| 2000 | 4700159 | 0.69 | 5.62 | 8.1449 | 5.66 | 42552.612
| 2500 | 9175845 | 0.63 | 5.65 | 8.9683 | 5.39 | 55855.2375
Table 2: 208Y/120 Three-Phase, Pad-Mounted Transformer
Information provided by Manufacturer
| Transformer kVA | Stock Number | % IR | %IX | X/R ratio | Transformer %Z | Calculated Fault Current (Amps)
| 75 | 7991359 | 1.16 | 2.49 | 2.1466 | 2.7 | 7719.4803
| 112.5 | 4700211 | 0.83 | 2.18 | 2.6265 | 2.33 | 13417.9807
| 150 | 4730212 | 1.17 | 3.03 | 2.5897 | 3.2 | 13026.6229
| 225 | 7991903 | 1.4 | 2.46 | 1.7571 | 2.7 | 23158.4408
| 300 | 4700214 | 0.81 | 3.11 | 3.84 | 1.75 | 47640.2211
| 500 | 9175340 | 0.83 | 3.53 | 4.25 | 2.17 | 64032.5552
| 750 | 7999497 | 0.85 | 5.79 | 6.8118 | 5.8 | 35935.5116
| 1000 | 8004518 | 0.83 | 5.89 | 7.0964 | 5.95 | 46706.0991
Table 3: 120/240 Single-Phase, Pad-Mounted and Overhead Transformers
Information provided by Manufacturer
| Transformer kVA | Stock Number | % IR | %IX | X/R ratio | Transformer %Z | Calculated Fault Current (Amps)
| 10 | N/A | N/A | N/A | N/A | 1.16 | 3591.954
| 25 | 4600612 | 0.92 | 1.5 | 1.6304 | 1.7 | 6127.451
| 50 | 9162314 | 0.8 | 1.4 | 1.75 | 1.6 | 13020.8333
| 75 | 4500356 | 0.97 | 1.1 | 1.134 | 1.49 | 20973.1544
| 100 | 9161902 | 0.98 | 1.2 | 1.2245 | 1.51 | 27593.819
| 167 | N/A | N/A | N/A | N/A | 1.55 | 44892.4731
| 250 | 4500115 | 0.7 | 2.37 | 3.3857 | 2.5 | 41666.6667
| 333 | 4500116 | 0.67 | 3.11 | 4.6418 | 3.2 | 43359.375
| 500 | 4500108 | 0.65 | 2.6 | 4 | 2.7 | 77160.4938
1 | Infinite Bus assumes unlimited primary short-circuit current. The power company's distribution system is constantly changing resulting in system impedances that change over time. An infinite bus eliminates the need to constantly re-evaluate short circuit current.
2 | Non-standard transformer
Table 4: Single-Phase Overhead Transformers used to create 480Y/277 banks
Information provided by Manufacturer
| Transformer kVA | Stock Number | % IR | %IX | X/R ratio | Transformer %Z | Calculated Fault Current (Amps)
| 25 | N/A | 1.2 | 1.4 | 1.1667 | 1.84 | 4908.5826
| 37.5 | N/A | 1.2 | 1.4 | 1.1667 | 1.84 | 7362.8738
| 50 | N/A | 1 | 1.4 | 1.4 | 1.72 | 10502.0836
| 75 | 4500364 | 1 | 1.2 | 1.2 | 1.55 | 17480.8876
| 100 | 4500124 | 0.84 | 1.64 | 1.9524 | 1.51 | 23925.2766
| 167 | N/A | 0.9 | 1.3 | 1.4444 | 1.58 | 38185.0443
| 250 | N/A | N/A | N/A | N/A | 1.7 | 53128.1877
| 333 | N/A | N/A | N/A | N/A | 1.6 | 75189.6676
Table 5: Single-Phase Overhead Transformers used to create three phase banks
208Y/120, 240 Closed Delta, 240 Open Delta
Information provided by Manufacturer
| Transformer kVA | Stock Number | % IR | %IX | X/R ratio | Transformer %Z | Calculated Fault Current (Amps)
| 25 | N/A | 1.2 | 1.4 | 1.1667 | 1.84 | 11327.4982
| 37.5 | 4500450 | 1.43 | 1.06 | 0.74126 | 1.78 | 17563.986
| 50 | N/A | 1 | 1.4 | 1.4 | 1.72 | 24235.5776
| 75 | 4500300 | 0.97 | 1.19 | 1.2268 | 1.54 | 40602.4611
| 100 | N/A | 0.86 | 1.28 | 1.4884 | 1.54 | 54136.6148
| 167 | N/A | 0.9 | 1.3 | 1.4444 | 1.58 | 88119.3329
| 500 | N/A | 1.1 | 1.6 | 1.4545 | 1.9 | 219395.7548
Table 6: 480/240 Single-Phase, Pad-Mounted and Overhead Transformers
Information provided by Manufacturer
| Transformer kVA | Stock Number | % IR | %IX | X/R ratio | Transformer %Z | Calculated Fault Current (Amps)
| 10 | N/A | 0.7975% | 1.363% | 1.724 | 1.41% | 1477.5414
| 25 | N/A | 1.263% | 1.573% | 1.2459 | 1.76% | 2959.2803
| 50 | N/A | 1.093% | 2.157% | 1.9862 | 2.11% | 4936.8088
| 75 | N/A | 0.98% | 2.193% | 2.2468 | 2.34% | 6677.3504
| 100 | N/A | 1.088% | 1.66% | 2.2958 | 1.34% | 15547.2637
| 167 | N/A | 0.815% | 2.814% | 3.4988 | 2.17% | 16033.0261
| 250 | N/A | 0.6837% | 3.104% | 4.5584 | 2.9% | 17959.7701
| 333 | N/A | 0.6387% | 3.161% | 5.0073 | 3.1% | 22379.0323
| 500 | N/A | 0.632% | 3.187% | 5.0427 | 3.2% | 32552.0833

## Overhead Transformer Fusing
Rocky Mountain Power and Pacific Power recommend customers de-energize electrical conductors when contact or faults are possible. These tables list common transformer fuses. The purpose of these fuses is to provide a means to de-energize transformers, prevent transformer damage, and isolate damaged transformers from electrical source. These fuses do not provide protection from arc flash or electrical contact.

## Underground Transformer Fusing
For more information on Cooper Power Bay-o-net and Isolation Links see Cooper Power Catalog.
Dual Sensing Bay-o-net fuses: Cooper Power Catalog Section 240-46
http://www.cooperindustries.com/content/dam/public/powersystems/resources/library/240_Fusing/24046.pdf
Isolation Links: Cooper Power Catalog Section 240-47
http://www.cooperindustries.com/content/dam/public/powersystems/resources/library/240_Fusing/24047.PDF
Dual Element Bay-o-net fuses: Cooper Power Catalog Section 240-48
http://www.cooperindustries.com/content/dam/public/powersystems/resources/library/240_Fusing/24048.pdf
Line-to-Grd or GrdWye-GrdWye Transformer Connections
Rocky Mountain Power and Pacific Power recommend customers de-energize electrical conductors when contact or faults are possible. These tables list common transformer fuses. The purpose of these fuses is to provide a means to de-energize transformers, prevent transformer damage, and isolate damaged transformers from electrical source. These fuses do not provide protection from arc flash or electrical contact.

## Updates (hidden)
Modifications Made to Spreadsheet
Date | Description of Changes made to Spreadsheet | Engineer

## Trans %Z (hidden)
Three Phase padmounts 480/277
SI# | Total# | KVA | HV Primary | LV Sevcondary | %Z | %RES | Tap or No Tap
4700090 | 37 | 75 | 12470GRD | 480Y/277 | 3.78 | 1.29 | NT | Transformers in "RED" have the lowest impedances, they were chosen to calculated faut current.
4700226 | 11 | 75 | 12470GRD | 480Y/277 | 3.77 | 1.26 | T
4710090 | 3 | 75 | 24940GRD | 480Y/277 | 1.62 | 0.99 | NT
9176439 | 10 | 75 | 34500GRD | 480Y/277 | 1.93 | 0.76 | T
4700092 | 31 | 150 | 12470GRD | 480Y/277 | 3.47 | 1.23 | NT
4700228 | 20 | 150 | 12470GRD | 480Y/277 | 3.18 | 1.04 | T
4710092 | 3 | 150 | 24940GRD | 480Y/277 | 3.34 | 1 | NT
7991368 | 10 | 150 | 20785GRD | 480Y/277 | 3.3 | 1.17 | T
4700229 | 5 | 225 | 12470GRD | 480Y/277 | 3.52 | 0.9 | T
4700093 | 12 | 225 | 12470GRD | 480Y/277 | 3.84 | 0.94 | NT
4730093 | 10 | 225 | 12470GRD/24940 | 480Y/277 | 4.04 | 1 | NT
4700094 | 41 | 300 | 12470GRD | 480Y/277 | 1.61 | 0.98 | NT
4700230 | 26 | 300 | 12470GRD | 480Y/277 | 1.99 | 0.9 | T
4730094 | 3 | 300 | 12470GRD | 480Y/277 | 4.09 | 0.94 | NT
7991369 | 3 | 300 | 20785GRD | 480Y/277 | 4.61 | 0.91 | T
4710094 | 3 | 300 | 24940GRD | 480Y/277 | 1.64 | 0.95 | NT
1004125 | 2 | 500 | 12470GRD/24940 | 480Y/277 | 4.57 | 0.97 | NT
4700095 | 43 | 500 | 12470GRD | 480Y/277 | 3.08 | 0.92 | NT
7991370 | 8 | 500 | 20785GRD | 480Y/277 | 4.56 | 0.98 | T
7991410 | 2 | 500 | 13200GRD | 480Y/277 | 1.94 | 1.04 | T
9176751 | 6 | 500 | 34500GRD | 480Y/277 | 5.01 | 1.08 | T
7991358 | 36 | 750 | 12470GRD | 480Y/277 | 5.72 | 0.88 | T
7991371 | 1 | 750 | 20785GRD | 480Y/277 | 5.63 | 0.9 | T
4900117 | 1 | 1000 | 7200GRDY/23470 | 480Y/277 | 5.64 | 0.82 | T
9175803 | 5 | 1000 | 20785GRD | 480Y/277 | 5.81 | 0.82 | T
7992849 | 2 | 1000 | 34500GRD | 480Y/277 | 5.9 | 0.89 | T
9174236 | 44 | 1000 | 12470GRD | 480Y/277 | 5.75 | 0.82 | T
9174749 | 1 | 1000 | 12470GRD | 480Y/277 | 5.45 | 0.81 | T
9174319 | 19 | 1500 | 12470GRD | 480Y/277 | 5.8 | 0.7 | T
1009571 | 1 | 1500 | 12470GRD/24940 | 480Y/277 | 5.53 | 0.8 | T
7992507 | 2 | 1500 | 24940GRD | 480Y/277 | 5.46 | 0.71 | T
7992508 | 1 | 2500 | 24940GRD | 480Y/277 | 5.74 | 0.6 | T
9174400 | 19 | 2500 | 12470GRD | 480Y/277 | 5.64 | 0.61 | T
9175845 | 1 | 2500 | 20785GRD | 480Y/277 | 5.39 | 0.55 | T
Three Phase Padmounts 208/120
SI# | Total# | KVA | HV Primary | LV Sevcondary | %Z | %RES | Tap or No Tap
4700210 | 90 | 75 | 12470GRD | 208Y/120 | 4.13 | 1.35 | NT
4700215 | 18 | 75 | 12470GRD | 208Y/120 | 4.43 | 1.47 | T
4710210 | 3 | 75 | 24940GRD | 208Y/120 | 3.15 | 1.28 | NT
7991359 | 5 | 75 | 20785GRD | 208Y/120 | 3.05 | 1.15 | T
4700212 | 113 | 150 | 12470GRD | 208Y/120 | 3.28 | 1.1 | NT
4700220 | 27 | 150 | 12470GRD | 208Y/120 | 3.23 | 1.12 | T
7991361 | 17 | 150 | 20785GRD | 208Y/120 | 3.69 | 1.17 | T
7991796 | 3 | 150 | 13200GRD | 208Y/120 | 3.49 | 1.11 | T
4700213 | 9 | 225 | 12470GRD | 208Y/120 | 3.84 | 0.99 | NT
4700221 | 3 | 225 | 12470GRD | 208Y/120 | 3.84 | 0.98 | T
7991363 | 3 | 225 | 20785GRD | 208Y/120 | 3.36 | 1 | T
4700214 | 80 | 300 | 12470GRD | 208Y/120 | 1.75 | 0.99 | NT
4700222 | 22 | 300 | 12470GRD | 208Y/120 | 1.86 | 0.96 | T
7991365 | 14 | 300 | 20785GRD | 208Y/120 | 3.54 | 1.01 | T
7991794 | 4 | 300 | 13200GRD | 208Y/120 | 4.36 | 0.95 | T
4700223 | 11 | 500 | 12470GRD | 208Y/120 | 2.23 | 1.13 | T
4700280 | 49 | 500 | 12470GRD | 208Y/120 | 2.35 | 1.07 | NT
4730275 | 2 | 500 | 12470GRD/24940 | 208Y/120 | 5.04 | 0.94 | T
7991366 | 7 | 500 | 20785GRD | 208Y/120 | 5.17 | 0.89 | T
9175340 | 1 | 500 | 20785GRD-Radial | 208Y/120 | 2.17 | 0.81 | T
7999497 | 6 | 750 | 12470GRD | 208Y/120 | 5.8 | 0.82 | T
Single Phase Pole Mount 120/240
| Ordered | KVA | Primary voltage | Secondary V | %Z | %RES
| 2 | 10 | 2400/4160Y | 120/240 | 1.68 | 1.16
| 4 | 10 | 7620/13200Y | 120/240 | 1.72 | 1.11
| 5 | 10 | 2400/4160YX7200/1247 | 120/240 | 2.05 | 1.37
| 16 | 10 | 14400/24940Y | 120/240 | 2.07 | 1.36
| 25 | 10 | 19920/34500Y | 120/240 | 2.64 | 1.54
| 182 | 10 | 12000/20780Y | 120/240 | 2.19 | 1.34
| 424 | 10 | 7200/12470Y | 120/240 | 1.79 | 1.34
| 12 | 25 | 2400/4160Y | 120/240 | 2.38 | 1.24
| 23 | 25 | 7620/13200Y | 120/240 | 2.6 | 1.29
| 29 | 25 | 2400/4160YX7200/1247 | 120/240 | 2.52 | 1.19
| 37 | 25 | 19920/34500Y | 120/240 | 3.13 | 1.34
| 59 | 25 | 14400/24940Y | 120/240 | 2.65 | 1.15
| 385 | 25 | 12000/20780Y | 120/240 | 2.46 | 1.03
| 1403 | 25 | 7200/12470Y | 120/240 | 2.47 | 1.15
| 11 | 50 | 19920/34500Y | 120/240 | 2.08 | 0.76
| 14 | 50 | 2400/4160YX7200/1247 | 120/240 | 1.81 | 0.74
| 15 | 50 | 14400/24940Y | 120/240 | 2.35 | 0.95
| 19 | 50 | 7620/13200Y | 120/240 | 1.77 | 0.76
| 22 | 50 | 2400/4160Y | 120/240 | 2.61 | 1.19
| 118 | 50 | 12000/20780Y | 120/240 | 2.5 | 0.93
| 550 | 50 | 7200/12470Y | 120/240 | 2.35 | 0.92
| 5 | 75 | 7620/13200Y | 120/240 | 2.31 | 0.94
| 11 | 75 | 12000/20780Y | 120/240 | 2.44 | 0.92
| 11 | 75 | 2400/4160YX7200/1247 | 120/240 | 2.07 | 0.9
| 113 | 75 | 7200/12470Y | 120/240 | 2.12 | 0.93
| 9 | 100 | 7200/12470Y | 120/240 | 1.6 | 0.59
| 17 | 100 | 12000/20780Y | 120/240 | 2.39 | 0.68
| 1 | 167 | 12000/20780Y | 120/240 | 2.2 | 0.68
| 3 | 167 | 2400/4160Y | 120/240 | 1.55 | 0.74
| 6 | 167 | 7200/12470Y | 120/240 | 1.87 | 0.67
Single phase Pole Mount 277 volt
| Ordered | KVA | Primary voltage | Secondary V | %Z | %RES
| 38 | 10 | 12000/20780Y | 277 | 1.96 | 1.26
| 17 | 10 | 14400/24940Y | 277 | 2.15 | 1.5
| 9 | 10 | 19920/34500Y | 277 | 2.26 | 1.45
| 191 | 10 | 7200/12470Y | 277 | 2.03 | 1.49
| 21 | 15 | 12000/20780Y | 277 | 2.25 | 1.28
| 30 | 15 | 7200/12470Y | 277 | 1.78 | 1.15
| 57 | 25 | 12000/20780Y | 277 | 2.24 | 1.03
| 12 | 25 | 14400/24940Y | 277 | 1.96 | 0.93
| 10 | 25 | 19920/34500Y | 277 | 2.83 | 1.27
| 198 | 25 | 7200/12470Y | 277 | 2.44 | 1.17
| 3 | 25 | 7620/13200Y | 277 | 2.57 | 1.31
| 14 | 38 | 12000/20780Y | 277 | 2.4 | 0.86
| 9 | 38 | 7200/12470Y | 277 | 2.74 | 1.04
| 51 | 50 | 12000/20780Y | 277 | 2.45 | 0.89
| 14 | 50 | 14400/24940Y | 277 | 1.87 | 0.72
| 28 | 50 | 19920/34500Y | 277 | 2.13 | 0.84
| 2 | 50 | 2400/4160Y | 277 | 1.6 | 1.01
| 191 | 50 | 7200/12470Y | 277 | 2.18 | 0.88
| 3 | 50 | 7200/12470YX14400/24 | 277 | 2.4 | 0.93
| 3 | 50 | 7620/13200Y | 277 | 1.89 | 0.91
| 20 | 75 | 12000/20780Y | 277 | 2.57 | 0.92
| 8 | 75 | 14400/24940Y | 277 | 2.06 | 0.8
| 22 | 75 | 19920/34500Y | 277 | 2.18 | 0.87
| 36 | 75 | 7200/12470Y | 277 | 1.89 | 0.79
| 9 | 75 | 7620/13200Y | 277 | 2.03 | 0.85
| 6 | 100 | 12000/20780Y | 277 | 2.39 | 0.65
| 9 | 100 | 14400/24940Y | 277 | 1.87 | 0.6
| 39 | 100 | 7200/12470Y | 277 | 1.63 | 0.59
| 3 | 167 | 7200/12470Y | 277 | 2.16 | 0.57

## Fusing Tables (hidden)
Overhead Transformer Fusing
Single f, Three f Y, Open D (Standard DP 011)
Transformer Size (kVA) | System Voltage (kV)
| 1 f | 2.4 | 4.16 | 7.2/7.62 | 12 | 14.4 | 19.9
| 3 f | 2.4 D 4.16 Y | 4.16 D 7.2 Y | 7.2 D 7.62 D 12.47 Y 13.2 Y | 12 D 20.8 Y | 14.4 D 24.9 Y | 19.9 D 34.5 Y
10 |  | 6T | 3KS* | 2KS* | 1KS* | 1KS* | 1KS*
15 |  | 8T | 6T | 3KS* | 2KS* | 2KS* | 1KS*
25 |  | 15T | 8T | 6T | 3KS* | 3KS* | 2KS*
37.5 |  | 20T | 12T | 8T | 6T | 6T | 3KS*
50 |  | 30T | 15T | 10T | 6T | 6T | 6T
75 |  | 40T | 30T | 15T | 8T | 8T | 6T
100 |  | 65T | 40T | 20T | 12T | 10T | 8T
167 |  | 100T | 65T | 30T | 20T | 15T | 12T
* High surge links (Chance MS, Kearny KS)
Overhead Transformer Fusing
Closed D Primary (Standard DP 011)
[8 empty] | Transformer Size (kVA) | System Voltage (kV)
[8 empty] | 3 f | 2.4 | 4.16 | 7.2 | 12
[8 empty] | (3-10) | 10T | 6T | 3KS* | 2KS*
[8 empty] | (3-15) | 15T | 8T | 6T | 3KS*
[8 empty] | (3-25) | 25T | 15T | 8T | 6T
[8 empty] | (3-37.5) | 40T | 20T | 12T | 8T
[8 empty] | (3-50) | 50T | 30T | 15T | 10T
[8 empty] | (3-75) | 80T | 40T | 25T | 15T
[8 empty] | (3-100) | 100T | 65T | 30T | 20T
[8 empty] | (3-167) | 200T | 100T | 50T | 30T
* High surge links (Chance MS, Kearny KS)
Underground Transformer Fusing
Single Phase Transformers (Line-to-Grd Voltage) (Standard DP 121)
[13 empty] | Transformer | System Voltage (kV)
[13 empty] | Rating (kVA) | 2.4 | 7.2 | 7.6 | 12 | 14.4 | 19.9
[13 empty] | 25 | 25DE | 6DE | 6DE | 5DE | 5DE | 3DS
[13 empty] | 37.5 | 40DE | 12DE | 12DE | 8DE | 6DE | 5DE
[13 empty] | 50 | 50DE | 15DE | 15DE | 12DE | 8DE | 5DE
[13 empty] | 75 | 65DS | 25DE | 25DE | 15DE | 12DE | 8DE
[13 empty] | 100 | 65DS | 25DE | 25DE | 15DE | 15DE | 12DE
[13 empty] | 167 | 140DS | 50DE | 50DE | 40DE | 25DE | 15DE
Note: DE = Dual Element (Cooper type 108), DS = Dual Sensing (Cooper type 358)
Underground Transformer Fusing
Three Phase Transformers (Line-to-Line Voltage) (Standard DP 131)
[13 empty] | Transformer | System Voltage (kV)
[13 empty] | Rating (kVA) | 4.16 | 7.2 | 12.47 | 20.8 | 24.9 | 34.5
[13 empty] | 75 | 25DE | 12DE | 6DE | 5DE | 5DE | 3DE
[13 empty] | 112.5 | 50DE | 15DE | 12DE | 8DE | 6DE | 5DE
[13 empty] | 150 | 65DS | 25DE | 15DE | 12DE | 12DE | 5DE
[13 empty] | 225 | 65DS | 40DE | 25DE | 15DE | 12DE | 8DE
[13 empty] | 300 | 65DS | 50DE | 25DE | 25DE | 40DE | 12DE
[13 empty] | 500 |  | 65DS | 50DE | 40DE | 40DE | 15DE
[13 empty] | 750 |  |  | 65DS | 50DE | 50DE | 25DS
[13 empty] | 1000 |  |  | 65DS | 65DE | 65DE | 25DS
[13 empty] | 1500 |  |  | 125HA | 65DS | 65DS | 50DS
[13 empty] | 2000 |  |  | 125HA | 100CS
[13 empty] | 2500 |  |  | 125HA | 125HA | 100CS | 100CS
Note: DE = Dual Element (Cooper type 108), DS = Dual Sensing (Cooper type 358), CS = Current Sensing (Cooper type 353), HA = High Ampere (Cooper type 361)
Terminal Pole Fusing for Unfused Transformer
Three Phase Transformers (Line-to-Line Voltage) (Standard DP 161)
[13 empty] | Transformer | System Voltage (kV)
[13 empty] | Rating (kVA) | 4.16 | 12.47 | 20.8 | 24.9 | 34.5
75
112
150
225
[13 empty] | 300 | 100T
[13 empty] | 500 | 140T
[13 empty] | 750 |  | 65T | 40T | 40T | 25T
[13 empty] | 1000 |  | 65T | 65T | 65T | 40T
[13 empty] | 1500 |  | 100T | 65T | 65T | 40T
[13 empty] | 2000 |  | 150E | 100T | 100T | 65T
[13 empty] | 2500 |  | 175E | 100T | 100T | 65T
Note: Unfused = Transformers without internal fusing